## Log
UPS / Generator Test Records
Authority |  | Adopted by Wabash Valley Communications under the authority of the Director.
Owner |  | IT Support Lead
Version / Dates |  | Version 1.0 Effective Date 2026-01-10 Next Review 2027-01-10
Classification |  | Restricted
Coverage / Scope |  | Covers regular testing of backup power for mission-critical systems: generator load tests, UPS battery-capacity verification, automatic-transfer tests, and any portable fallback. Test frequency follows the Power Resilience Configuration Documentation. Covers 2026-01-01 to 2026-12-31. Reviewer (role): IT Support Lead.
Test Records
Entry # | Date | Unit tested | Test type | Result (measured vs required) | Deficiency & follow-up
001 | 2026-01-10 | Standby generator G-1 | Generator load test | Pass; 45-minute load-bank test, 72-hour fuel | None
002 | 2026-01-10 | UPS-1 and UPS-2 | UPS battery capacity | Pass; 15 and 12 min at full load | None
003 | 2026-04-12 | Automatic transfer switch | Automatic transfer test | Pass; transferred to generator in 8 seconds | None
004 | 2026-07-11 | Standby generator G-1 | Generator load test | Fail; would not start on first attempt | Starter battery replaced; retested and passed 2026-07-12 (R-058)
Findings
Quarterly tests passed except a July generator start failure, corrected by starter-battery replacement and retested the next day (R-058).
Sign-off
Role | Name | Signature | Date
Reviewed by (IT Support Lead) | (on file) | (on file) | 2026-07-12
Approved by (Director) | Anthony Reyes | /s/ Anthony Reyes | 2026-07-12
Retention
Retention: 3 years, stored in the secure records system.
Source Authority
NENA-STA-040.2-2024: §5.3 (Availability); §6.7.2 (Environmental Controls)
NIST SP 800-53 Rev. 5: CP-8, PE-9, PE-11
Revision History
Version | Date | Author | Summary of Change
1.0 | 2026-01-10 | IT Support Lead | Initial issue