Single-Point-of-Failure Assessment Record

Assessment date: 2026-04-17 Assessor (role): Information Security Analyst Scope: the Agency’s systems and paths reviewed for single points of failure, read against the System Redundancy Design Documentation Owner: Information Security Analyst Classification: Restricted

## 1. Executive Summary

This record identifies single points of failure in the Agency’s infrastructure, such as a lone cable route, a single power feed, or one core switch, and records the redundancy decision and priority for each. Two single points of failure remain on the critical path. Both fiber routes share a conduit at the building entrance, and the ESInet border gateway is not yet redundant. A diverse entrance and an N+1 gateway are in engineering, with interim paths live.

## 2. Findings

| SPOF ID | Single point of failure (system / path) | Impact / priority | Redundancy treatment & decision |
| --- | --- | --- | --- |
| S-01 | Both fiber routes share one conduit for ~200 ft at the building entrance | High | Trench a diverse building entrance; interim microwave backup path is in service |
| S-02 | Single ESInet border gateway at the primary site | Med | Deploy an N+1 gateway pair; failover tested quarterly |

## 3. Remediation Tracking

| SPOF ID | Owner (role) | Action | Due date | Status |
| --- | --- | --- | --- | --- |
| S-01 | IT Team | Engineer a diverse building entrance; keep the microwave path live | 2026-08-15 | In progress |
| S-02 | Information Security Analyst | Install a redundant border gateway and add it to the quarterly failover test | 2026-06-30 | In progress |

## Profile Scaling Notes

| PSAP Profile | Minimum-viable implementation |
| --- | --- |
| Large (25+, dedicated IT/security) | Redundancy is mapped from network and facility diagrams, single points of failure are rated by impact, and treatments are prioritized and tracked. |

Source Authority NENA-STA-040.2-2024: §5.3 (Availability); §6.14 (Network Availability); §6.15 (Diversity) NIST SP 800-53 Rev. 5: CP-2, CP-7, PE-9, SC-5

## Sign-off

| Role | Name | Signature | Date |
| --- | --- | --- | --- |
| Information Security Analyst | Raymond Osei | /s/ Raymond Osei | 2026-04-17 |
| Director | Dr. Lisa Park | /s/ Dr. Lisa Park | 2026-04-17 |

## Revision History

| Version | Date | Author | Summary of Change |
| --- | --- | --- | --- |
| 1.0 | 2026-04-17 | Information Security Analyst | Initial issue |