Power Resilience Configuration Documentation

Authority: Adopted by Tri-River Regional 911 Center under the authority of the Director. Version: 1.0 Effective Date: 2026-04-17 Next Review: 2027-04-17 Owner: IT Team Classification: Restricted

## 1. Purpose and Scope

This record documents the as-built power resilience protecting the Agency’s mission-critical systems: UPS and generator capacity, the runtime each provides at full load, the managed-shutdown procedure beyond generator runtime, and the limited-capability alternatives for extended outages. It is the as-built evidence behind the continuity plan; response coordination sits in the Continuity of Operations Plan.

## 2. System Identification

| Field | Value |
| --- | --- |
| System name | Backup power (UPS and standby generator) |
| Environment | production |
| Location | the Tri-River primary center (both floors) |
| Owner (role) | IT Team |
| Asset ID | PWR-DC-01 |

## 3. Current Configuration

| Unit | Capacity / runtime at full load | Systems and areas protected |
| --- | --- | --- |
| 40 kVA N+1 online UPS | ~30 min at full load | Both dispatch floors, data center, ESInet edge |
| 2 x 250 kW diesel (N+1) | 96 h at load; 2,000 gal; automatic transfer | Entire facility: dispatch, data center, HVAC |
| 100 kW trailer generator (contracted) | 4 h delivery SLA | Facility load if both standby units fail |

Managed shutdown beyond generator runtime. When generator runtime is exhausted, systems are shut down in a defined order to protect data and equipment, and staff move to the alternate or limited-capability option. The response is coordinated under the Continuity of Operations Plan.

## 4. Approved Settings and Deviation Log

| System tier | Required runtime | Deviation? | Approved by (role) | Date |
| --- | --- | --- | --- | --- |
| Dispatch & data center | 72 h | N | IT Team | 2026-04-17 |
| Full facility | 24 h | N | IT Team | 2026-04-17 |

## 5. Validation and Review

Validated against the Continuity of Operations Plan and the required runtimes at least annually by the IT Team. Test evidence is recorded in the UPS / Generator Test Records.

## Profile Scaling Notes

| PSAP Profile | Minimum-viable implementation |
| --- | --- |
| Large (25+, dedicated IT/security) | The record is generated from facility and power-monitoring systems, with runtimes validated against measured load and reviewed on a set cycle. |

Source Authority NENA-STA-040.2-2024: §5.3 (Availability); §6.7.2 (Environmental Controls) NIST SP 800-53 Rev. 5: CP-8, PE-9, PE-11, PE-12

## Approval Signatures

| Role | Name | Signature | Date |
| --- | --- | --- | --- |
| IT Team | Sam Whitfield | /s/ Sam Whitfield | 2026-04-17 |
| Information Security Analyst | Raymond Osei | /s/ Raymond Osei | 2026-04-17 |

## Change History

| Version | Date | Author | Summary of Change |
| --- | --- | --- | --- |
| 1.0 | 2026-04-17 | IT Team | Initial issue |