Power Resilience Configuration Documentation

Authority: Adopted by Wabash Valley Communications under the authority of the Director. Version: 1.0 Effective Date: 2026-03-06 Next Review: 2027-03-06 Owner: IT Support Lead Classification: Restricted

## 1. Purpose and Scope

This record documents the as-built power resilience protecting the Agency’s mission-critical systems: UPS and generator capacity, the runtime each provides at full load, the managed-shutdown procedure beyond generator runtime, and the limited-capability alternatives for extended outages. It is the as-built evidence behind the continuity plan; response coordination sits in the Continuity of Operations Plan.

## 2. System Identification

| Field | Value |
| --- | --- |
| System name | Backup power (UPS and standby generator) |
| Environment | production |
| Location | the Wabash Valley dispatch center |
| Owner (role) | IT Support Lead |
| Asset ID | PWR-CORE-01 |

## 3. Current Configuration

| Unit | Capacity / runtime at full load | Systems and areas protected |
| --- | --- | --- |
| 10 kVA online UPS | ~45 min at full load | Dispatch consoles, CAD/RMS servers, network core |
| 60 kW diesel standby | 72 h at load; 400 gal; automatic transfer | Full dispatch center, server room, HVAC |
| 15 kW towable generator | extends runtime; manual connect | Server room and one console in an extended outage |

Managed shutdown beyond generator runtime. When generator runtime is exhausted, systems are shut down in a defined order to protect data and equipment, and staff move to the alternate or limited-capability option. The response is coordinated under the Continuity of Operations Plan.

## 4. Approved Settings and Deviation Log

| System tier | Required runtime | Deviation? | Approved by (role) | Date |
| --- | --- | --- | --- | --- |
| Dispatch & servers | 24 h | N | IT Support Lead | 2026-03-06 |
| Full facility | 8 h | N | IT Support Lead | 2026-03-06 |

## 5. Validation and Review

Validated against the Continuity of Operations Plan and the required runtimes at least annually by the IT Support Lead. Test evidence is recorded in the UPS / Generator Test Records.

## Profile Scaling Notes

| PSAP Profile | Minimum-viable implementation |
| --- | --- |
| Medium (6–25, shared county IT) | Shared county IT documents capacities and runtimes per system, and reviews the record after each power test. |

Source Authority NENA-STA-040.2-2024: §5.3 (Availability); §6.7.2 (Environmental Controls) NIST SP 800-53 Rev. 5: CP-8, PE-9, PE-11, PE-12

## Approval Signatures

| Role | Name | Signature | Date |
| --- | --- | --- | --- |
| IT Support Lead | Dana Mercer | /s/ Dana Mercer | 2026-03-06 |
| Director | Anthony Reyes | /s/ Anthony Reyes | 2026-03-06 |

## Change History

| Version | Date | Author | Summary of Change |
| --- | --- | --- | --- |
| 1.0 | 2026-03-06 | IT Support Lead | Initial issue |