Power Resilience Configuration Documentation

Authority: Adopted by Hickory County 911 under the authority of the Director. Version: 1.0 Effective Date: 2026-02-13 Next Review: 2027-02-13 Owner: County IT Administrator Classification: Restricted

## 1. Purpose and Scope

This record documents the as-built power resilience protecting the Agency’s mission-critical systems: UPS and generator capacity, the runtime each provides at full load, the managed-shutdown procedure beyond generator runtime, and the limited-capability alternatives for extended outages. It is the as-built evidence behind the continuity plan; response coordination sits in the Continuity of Operations Plan.

## 2. System Identification

| Field | Value |
| --- | --- |
| System name | Backup power (UPS and standby generator) |
| Environment | production |
| Location | the primary dispatch center |
| Owner (role) | County IT Administrator |
| Asset ID | PWR-01 |

## 3. Current Configuration

| Unit | Capacity / runtime at full load | Systems and areas protected |
| --- | --- | --- |
| 1.5 kVA rack UPS | ~20 min at full load | Dispatch console, radio gateway, core switch |
| 12 kW propane standby | 48 h at load; 250 gal on-site | Dispatch, equipment-room HVAC, lighting |
| None; manual UPS battery swap | bridges console only, ~15 min | Single dispatch console during changeover |

Managed shutdown beyond generator runtime. When generator runtime is exhausted, systems are shut down in a defined order to protect data and equipment, and staff move to the alternate or limited-capability option. The response is coordinated under the Continuity of Operations Plan.

## 4. Approved Settings and Deviation Log

| System tier | Required runtime | Deviation? | Approved by (role) | Date |
| --- | --- | --- | --- | --- |
| Dispatch console & radio | 8 h | N | County IT Administrator | 2026-02-13 |
| Facility (HVAC, lighting) | 4 h | N | County IT Administrator | 2026-02-13 |

## 5. Validation and Review

Validated against the Continuity of Operations Plan and the required runtimes at least annually by the County IT Administrator. Test evidence is recorded in the UPS / Generator Test Records.

## Profile Scaling Notes

| PSAP Profile | Minimum-viable implementation |
| --- | --- |
| Small (1–5 dispatchers, no in-house IT) | One person records the UPS and generator sizes, what each protects, and how long they last, and keeps a short managed-shutdown checklist. |

Source Authority NENA-STA-040.2-2024: §5.3 (Availability); §6.7.2 (Environmental Controls) NIST SP 800-53 Rev. 5: CP-8, PE-9, PE-11, PE-12

## Approval Signatures

| Role | Name | Signature | Date |
| --- | --- | --- | --- |
| County IT Administrator | Marcus Reed | /s/ Marcus Reed | 2026-02-13 |
| Director | Tracy Holloway | /s/ Tracy Holloway | 2026-02-13 |

## Change History

| Version | Date | Author | Summary of Change |
| --- | --- | --- | --- |
| 1.0 | 2026-02-13 | County IT Administrator | Initial issue |